{"text_format":"1","workbook":"xlsx","n_sheets":1,"sheets":["Ekspanzija - proračun"],"not_rendered":{"charts":0,"images":2,"macros":0,"external_links":0,"defined_names":0,"comments":1,"pivot_tables":0},"unopened":[],"bounds":{"document_bytes":16777216,"sheet_cells":100000,"rows_first":2000,"rows_last":500,"rows_between":2000,"halvings":0,"cell_chars":16384,"cell_head_chars":4096},"cells_cut":0,"cells_raw":0,"read":"whole","date_system":"1900"}

{"sheet":"Ekspanzija - proračun","index":0,"n_rows":23,"n_cols":24,"rows_kept":23,"cut":false,"hidden":false,"merged":[[22,2,24,7],[22,9,24,12],[1,1,1,13],[4,6,4,7],[6,6,6,7],[8,6,8,7],[13,2,13,7],[13,9,14,12],[14,2,14,7],[15,2,17,7],[15,9,17,12],[20,2,20,7],[20,9,21,12],[21,2,21,7]]}
[]
[null,"Proračun minimalnog volumena ekspanzijske posude"]
[]
[]
[null,null,"Ukupan volumen vode u sistemu [L]:",null,null,null,1300,null,null,"Potreban primarni tlak eksp. posude:",null,null,{"$f":"X7","v":1},"bar"]
[]
[null,null,"Najviša točka instalacije od eksp. posude [m]:",null,null,null,null,null,null,"Projektni krajnji tlak sistema:",null,null,{"$f":"G9-0.5","v":2.5},"bar",null,null,null,null,null,null,null,"do 10m","do 10m",{"$f":"IF(W7=\"do 10m\",1,IF(W7=\"10 - 15m\",1.5,IF(W7=\"15 - 20m\",2)))","v":1}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10 - 15m"]
[null,null,"Nazivni tlak sigurnosnog ventila  [bar]:",null,null,null,3,null,null,"Volumen širenja vode:",null,null,{"$f":"X11*G5/100","v":36.4},"L",null,null,null,null,null,null,null,"15 - 20m"]
[]
[null,null,"Opseg temperature sistema  [°C]:",null,null,null,null,null,null,"Volumen zalihe vode:",null,null,{"$f":"IF(G5*0.005 > 3,G5*0.005,3)","v":6.5},"L",null,null,null,null,null,null,null,"10 - 70°C","10 - 80°C",{"$f":"IF(W11=\"10 - 70°C\",2.2,IF(W11=\"10 - 80°C\",2.8,IF(W11=\"10 - 90°C\",3.5,IF(W11=\"10 - 100°C\",4))))","v":2.8}]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10 - 80°C"]
[null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,null,"10 - 90°C"]
[null,null,"Potreban volumen ekspanzijske posude",null,null,null,null,null,null,"Odnos između volumena ekspanzijske posude i ukupnog volumena sistema:",null,null,null,null,null,null,null,null,null,null,null,"10 - 100°C"]
[null,null,{"$f":"CONCATENATE(\"pri primarnom tlaku od \",M5,IF(OR(M5=1,M5=2),\",0 bar:\",\" bar:\"))","v":"pri primarnom tlaku od 1,0 bar:"}]
[null,null,{"$f":"($M$9+$M$11)*($M$7+$M$5)/($M$7-$M$5)","v":100.10000000000001},null,null,null,null,null,null,{"$f":"C16/$G$5","v":7.7000000000000013E-2}]
[]
[]
[]
[]
[null,null,"Potreban volumen ekspanzijske posude",null,null,null,null,null,null,"Odnos između volumena ekspanzijske posude i ukupnog volumena sistema:"]
[null,null,"pri tvorničkom tlaku od 1,5 bar:"]
[null,null,{"$f":"($M$9+$M$11)*($M$7+1.5)/($M$7-1.5)","v":171.6},null,null,null,null,null,null,{"$f":"C23/$G$5","v":0.13200000000000001}]